## MCC60.1 si 2
| Rev. | Item |  | Cables tag | Consumer | P | U | cos Ø | ƞm | Starting method | Starting current Istart/Ib | Ib | In | Conductor | Cable insulation | S | Cable type | No. Of cable | Icable | Cable installation methode
| Rev. | Nr. |  | Tag cablu | Consumator |  |  |  |  | Metoda de pornire | Crt.de pornire Istart/Ib |  |  | Conductor | Izolatie cablu |  | Tip cablu | Nr. cabl. |  | Mod de instalare
[6 empty] | [kW] | [V] | [/] | [%] | [-] | [-] | [A] | [A] | [-] | [-] | [mm2] | [mm2] | [A] | [A] | [-]
| 0 | 1 |  | 2 | 3 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 17 | 18
MCC60,1 | 0 | 1 | 1Q011 | BE62.WP01 | BE62 | 110 | 400 | 0.87 | 0.92 | VFD | 1.5 | 198.6001 | 240 | Cu | PVC | 95 | 3x95+50 | 1 | 238 | E
|  |  | 1Q012 | 2: BE62-1.WP02; 3: BE62-1; 5: 1.5; 6: 400; 9: `DOL; 10: 5
| 0 | 2 | 1Q021 | SF1 BE62.WP01 | SF1 BE62 | 2.2 | 400 | 0.87 | 0.95 | DOL | 5 | 3.8466 | 4.4 | Cu | PVC | 2.5 | 4x2.5 | 1 | 5 | E
| 0 | 3 | 1Q031 | BE63.WP01 | BE63 | 160 | 400 | 0.87 | 0.95 | VFD | 1.5 | 279.7506 | 320 | Cu | PVC | 95 | 3x95+50 | 1 | 5 | E
|  |  | 1Q032 | 2: BE63-1.WP02; 3: BE63-1; 5: 1.5; 6: 400
| 0 | 4 | 1Q041 | SF1 BE63.WP01 | SF1 BE63 | 2.2 | 400 | 0.87 | 0.95 | DOL | 5 | 3.8466 | 220 | Cu | PVC | 2.5 | 4x2.5 | 1 | 196 | E
| 0 | 5 | 1Q051 | CC61.WP01 | CC61 | 55 | 400 | 0.87 | 0.95 | SST | 3 | 96.1643 | 100 | Cu | PVC | 35 | 3x35+16 | 1 | 126 | E
| 0 | 6 | 1Q061 | CC68.WP01 | CC68 | 55 | 400 | 0.87 | 0.95 | SST | 3 | 78.6799 | 90 | Cu | PVC | 35 | 3x25+16 | 1 | 101 | E
| 0 | 7 | 1Q071 | CC63.WP01 | CC63 | 18.5 | 400 | 0.87 | 0.95 | SST | 3 | 32.3462 | 17 | Cu | PVC | 10 | 4x10 | 1 | 60 | E
| 0 | 8 | 1Q081 | CC64.WP01 | CC64 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E
| 0 | 9 | 1Q091 | VA62 M1.WP01 | VA62 M1 | 0.75 | 400 | 0.87 | 0.95 | SST | 3 | 1.3113 | 1.6 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 10 | 1Q101 | VA62 M2.WP01 | VA62 M2 | 0.75 | 400 | 0.87 | 0.95 | SST | 3 | 1.3113 | 1.6 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 11 | 1Q111 | VA62 M3.WP01 | VA62 M3 | 0.75 | 400 | 0.87 | 0.95 | SST | 3 | 1.3113 | 1.6 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 12 | 1Q121 | VA62 M4.WP01 | VA62 M4 | 0.75 | 400 | 0.87 | 0.95 | SST | 3 | 1.3113 | 1.6 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 13 | 1Q131 | SGCC61.WP01 | SGCC61 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 14 | 1Q141 | SGCC64.WP01 | SGCC64 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 15 | 1Q151 | Tripper BC6-SB8.WP02 | Tripper BC6-SB8 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 16 | DOAR PARTEA DINSPRE MOTOR PLUS ALIMENTAREA MOTORULUI | BC6-SB8.WP02 | BC6-SB8 | 75 | 400 | 0.87 | 0.95 | SST | 3 | 131.1331 | 150 | Cu | PVC | 50 | 3x50+25 | 1 | 153 | E
MCC60,2 | 0 | 17 | 2Q011 | BE64.WP01 | BE64 | 90 | 400 | 0.87 | 0.95 | VFD | 1.5 | 157.3597 | 180 | Cu | PVC | 50 | 3x50+25 | 1 | 153 | E
|  |  | 2Q012 | 2: BE64-1.WP02; 3: BE64-1; 5: 1.5; 6: 400
| 0 | 18 | 2Q021 | SF1 BE64.WP01 | SF1 BE64 | 2.2 | 400 | 0.87 | 0.95 | DOL | 5 | 3.8466 | 4.4 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 19 | 2Q031 | VA64 M1.WP01 | VA64 M1 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 20 | 2Q041 | VA64 M2.WP01 | VA64 M2 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 21 | 2Q051 | CC69.WP01 | CC69 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E
| 0 | 22 | 2Q061 | CC70.WP01 | CC70 | 55 | 400 | 0.87 | 0.95 | SST | 3 | 96.1643 | 100 | Cu | PVC | 35 | 3x35+16 | 1 | 126 | E
| 0 | 23 | 2Q071 | CC65.WP01 | CC65 | 30 | 400 | 0.87 | 0.95 | SST | 3 | 52.4532 | 60 | Cu | PVC | 16 | 4x16 | 1 | 80 | E
| 0 | 24 | 2Q081 | CC66.WP01 | CC66 | 30 | 400 | 0.87 | 0.95 | SST | 3 | 52.4532 | 60 | Cu | PVC | 16 | 4x16 | 1 | 80 | E
| 0 | 25 | 2Q091 | CC67.WP01 | CC67 | 30 | 400 | 0.87 | 0.95 | SST | 3 | 52.4532 | 60 | Cu | PVC | 16 | 4x16 | 1 | 80 | E
| 0 | 26 | 2Q101 | SGSB61.1.WP01 | SGSB61.1 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 27 | 2Q111 | SGSB61.2.WP01 | SGSB61.2 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 28 | 2Q121 | SGSB61.3.WP01 | SGSB61.3 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 29 | 2Q131 | SGSB61.4.WP01 | SGSB61.4 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 30 | 2Q141 | SGSB62.1.WP01 | SGSB62.1 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 31 | 2Q151 | SGSB62.2.WP01 | SGSB62.2 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 32 | 2Q161 | SGSB62.3.WP01 | SGSB62.3 | 0.55 | 400 | 0.87 | 0.95 | SST | 2.2 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 33 | 2Q171 | SGSB62.4.WP01 | SGSB62.4 | 0.55 | 400 | 0.87 | 0.95 | SST | 2.2 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 34 | 2Q181 | SGSB63.1.WP01 | SGSB63.1 | 0.55 | 400 | 0.85 | 0.95 | SST | 3 | 0.98427 | 16 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 35 | 2Q191 | SGSB63.2.WP01 | SGSB63.2 | 0.55 | 400 | 0.85 | 0.95 | SST | 3 | 0.98427 | 16 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 36 | 2Q201 | SGSB63.3.WP01 | SGSB63.3 | 0.55 | 400 | 0.85 | 0.95 | SST | 3 | 0.98427 | 16 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 37 | 2Q211 | SGSB63.4.WP01 | SGSB63.4 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 38 | 2Q221 | SGSB64.1.WP01 | SGSB64.1 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 39 | 2Q231 | SGSB64.2.WP01 | SGSB64.2 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 40 | 2Q241 | SGSB64.3.WP01 | SGSB64.3 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 41 | 2Q251 | SGSB64.4.WP01 | SGSB64.4 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 42 | 2Q261 | SGSB65.1.WP01 | SGSB65.1 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 43 | 2Q271 | SGSB65.2.WP01 | SGSB65.2 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 44 | 2Q281 | SGSB65.3.WP01 | SGSB65.3 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 45 | 2Q291 | SGSB65.4.WP01 | SGSB65.4 | 0.55 | 400 | 0.87 | 0.95 | SST | 3 | 0.96164 | 1.2 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 46 | 2Q301 | SA61.WP01 | SA61 | 18.5 | 400 | 0.87 | 0.95 | SST | 3 | 32.3462 | 36 | Cu | PVC | 10 | 4x10 | 1 | 60 | E
| 0 | 47 | 2Q311 | SA62.WP01 | SA62 | 18.5 | 400 | 0.87 | 0.95 | SST | 3 | 32.3462 | 36 | Cu | PVC | 10 | 4x10 | 1 | 60 | E
| 0 | 48 | 2Q321 | SA63.WP01 | SA63 | 18.5 | 400 | 0.87 | 0.95 | SST | 3 | 32.3462 | 36 | Cu | PVC | 10 | 4x10 | 1 | 60 | E
| 0 | 49 | 2Q331 | SA64.WP01 | SA64 | 18.5 | 400 | 0.87 | 0.95 | SST | 3 | 32.3462 | 36 | Cu | PVC | 10 | 4x10 | 1 | 60 | E
| 0 | 50 | 2Q341 | SA65.WP01 | SA65 | 18.5 | 400 | 0.87 | 0.95 | SST | 3 | 32.3462 | 36 | Cu | PVC | 10 | 4x10 | 1 | 60 | E
| 0 | 51 | 2Q351 | P SA61.WP01 | P SA61 | 1.5 | 400 | 0.87 | 0.95 | DOL | 5 | 2.6227 | 3.7 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 52 | 2Q361 | P SA62.WP01 | P SA62 | 1.5 | 400 | 0.87 | 0.95 | DOL | 5 | 2.6227 | 3.7 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 53 | 2Q371 | P SA63.WP01 | P SA63 | 1.5 | 400 | 0.87 | 0.95 | DOL | 5 | 2.6227 | 3.7 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 54 | 2Q381 | P SA64.WP01 | P SA64 | 1.5 | 400 | 0.87 | 0.95 | DOL | 5 | 2.6227 | 3.7 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 55 | 2Q391 | P SA65.WP01 | P SA65 | 1.5 | 400 | 0.87 | 0.95 | DOL | 5 | 2.6227 | 3.7 | Cu | PVC | 2.5 | 4x2.5 | 1 | 25 | E
| 0 | 56 | 2Q401 | Fan SB61-1.WP01 | Fan SB61-1 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E
| 0 | 57 | 2Q411 | Fan SB61-2.WP01 | Fan SB61-2 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E
| 0 | 58 | 2Q421 | Fan SB62-1.WP01 | Fan SB62-1 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E
| 0 | 59 | 2Q431 | Fan SB62-2.WP01 | Fan SB62-2 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E
| 0 | 60 | 2Q441 | Fan SB63-1.WP01 | Fan SB63-1 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E
| 0 | 61 | 2Q451 | Fan SB63-2.WP01 | Fan SB63-2 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E
| 0 | 62 | 2Q461 | Fan SB64-1.WP01 | Fan SB64-1 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E
| 0 | 63 | 2Q471 | Fan SB64-2.WP01 | Fan SB64-2 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E
| 0 | 64 | 2Q481 | Fan SB65-1.WP01 | Fan SB65-1 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E
| 0 | 65 | 2Q491 | Fan SB65-2.WP01 | Fan SB65-2 | 37 | 400 | 0.87 | 0.95 | SST | 3 | 64.6923 | 70 | Cu | PVC | 25 | 3x25+16 | 1 | 101 | E

## TGD
TGD
| Curent | Nr poli
Sosire din trafo 2000KVA (prin bare) | 3200 | 3 | 3P+PEN
Baterie de compensare | 1000 | 3 | 3P+PEN
MCC60.1 | 1600 | 3 | 3P+PEN
MCC60.2 | 1600 | 3 | 3P+PEN
Casa pompe incendiu | 125 | 4 | 3P+N+PE
Tablou iluminat, prize si auxiliare | 125 | 4 | 3P+N+PE
REZERVA | 125 | 3 | 3P+PEN
REZERVA | 80 | 3 | 3P+PEN
REZERVA | 40 | 3 | 3P+PEN
TABLOU ILUMINAT PRIZE AUXILIARE
Scari acces siloz SB61 | 10 | 2P |  | Comanda cu contactor si crepuscular
Scari acces siloz SB62 | 10 | 2P |  | Comanda cu contactor si crepuscular
Scari acces siloz SB63 | 10 | 2P |  | Comanda cu contactor si crepuscular
Scari acces siloz SB64 | 10 | 2P |  | Comanda cu contactor si crepuscular
Scari acces siloz SB65 | 10 | 2P |  | Comanda cu contactor si crepuscular
Turn TW 6B (BE62) | 16 | 2P |  | Comanda cu contactor si comutator local
Turn TW 6C (BE63-64) | 16 | 2P |  | Comanda cu contactor si comutator local
Pasarela CC61 | 10 | 2P |  | Comanda cu contactor si comutator local
Pasarela CC63 | 10 | 2P |  | Comanda cu contactor si comutator local
Pasarela CC64 | 10 | 2P |  | Comanda cu contactor si comutator local
Pasarela CC68-70 | 10 | 2P |  | Comanda cu contactor si comutator local
Tunel CC69 | 10 | 2P |  | Comanda cu contactor si comutator local
Tunel CC65 | 10 | 2P |  | Comanda cu contactor si comutator local
Tunel CC66 | 10 | 2P |  | Comanda cu contactor si comutator local
Tunel CC67 | 10 | 2P |  | Comanda cu contactor si comutator local
Balizaj TW6B | 10 | 2P |  | Comanda cu contactor si crepuscular
Balizaj TW6C | 10 | 2P |  | Comanda cu contactor si crepuscular
Camera MT | 10 | 2P |  | Intrerupator
Camera Trafo | 10 | 2P |  | Intrerupator
Camera MCC | 10 | 2P |  | Intrerupator
Exterior Cladire | 10 | 2P |  | Intrerupator
Rezerva iluminat | 10 | 2P |  | Intrerupator
Rezerva iluminat | 10 | 2P |  | Comanda cu contactor si crepuscular
Rezerva iluminat | 10 | 2P |  | Comanda cu contactor si crepuscular
Ventilatie Fortata Trafo | 10 | 3P |  | Comanda cu contactor si termostat
Ventilatie Fortata MCC | 10 | 3P |  | Comanda cu contactor si termostat
Prize MT | 16 | 2P
Prize MCC | 16 | 2P
Prize MCC | 16 | 2P
AC1 MCC | 16 | 4P
AC2 MCC | 16 | 4P
Tablou servicii interne MT | 16 | 2P
Tablou servicii interne MT | 16 | 2P |  | Descriere in atasament